## SUMMARY
CONDITION MONITORING REPORT
Sl. No. | EQUIPMENTS | Last reading date | CRITICAL LIMIT (mm/sec) | MAX. VIB. (Vel in mm/ Sec) | CONDITION IN JUNE'18 | CONDITION IN MAY '18 | CONDITION IN APR '18 | CONDITION IN MAR '18 | CONDITION IN FEB '18 | CONDITION IN JAN '18 | CONDITION IN DEC '17 | CONDITION IN NOV '17 | CONDITION IN OCT '17 | CONDITION IN SEP '17 | CONDITION IN AUG '17 | CONDITION IN JUL '17 | CONDITION IN JUN '17 | CONDITION IN MAY '17 | CONDITION IN APR '17 | REMARKS
1 | COOLING WATER PUMP-1 | 28.05.18 | 11.2 | 2 |  | NORMAL/ALARM | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | *Vibration levels are with in the limit. **Gear train gear meshing frequencies (204.5Hz) are transmitting to roll
2 | BOILER FEED PUMP-2 | 08.06.18 | 11.2 | 2.5 | NORMAL/ALARM | NORMAL | NORMAL | ALERT | ALERT | NORMAL/ALARM | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | *Vibration levels are in satisfactory condition.
3 | KA#3 CHEST PUMP-2 | 11.05.18 | 7.1 | 2.6 |  | NORMAL/ALARM | NORMAL | ALERT | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | NORMAL | *Vibration levels are in satisfactory condition. *Spectrum analysis is indicating 24.6 Hz at roll both bearings.
INTERNATIONAL PAPER APPM LIMITED - KADIYAM

## CWP-1
CW PUMP-1 |  |  | SUMMARY
VELOCITY (mm/sec) |  |  | RMS
Date | NORMAL BELOW | ALARM ABOVE | MOTOR NDE-H | MOTOR NDE-V | MOTOR NDE-A | MOTOR DE-H | MOTOR DE-V | MOTOR DE-A | Max Vib. | STATUS | OBSERVATIONS & ANALYSIS | RECOMMENDATIONS
20.04.17 | 7.1 | 11.2 | 1.1 | 0.8 | 0.8 | 1.2 | 0.8 | 1 | 1.1 | NORMAL | *After grouting & base frame replacement, vibration levels came down to 1.2 mm/sec from 6.2 mm/sec. | * Monitor the vibration trend levels.
25.05.17 | 7.1 | 11.2 | 1.1 | 1 | 0.9 | 1.1 | 0.6 | 1.2 | 1.2 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
09.06.17 | 7.1 | 11.2 | 1.8 | 1 | 0.9 | 1.3 | 0.9 | 0.8 | 1.8 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
27.07.17 | 7.1 | 11.2 | 1.3 | 0.9 | 1 | 1.6 | 1 | 1 | 1.6 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
26.08.17 | 7.1 | 11.2 | 2 | 1.1 | 1.3 | 2 | 1.5 | 1 | 2 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
20.09.17 | 7.1 | 11.2 | 2.1 | 1.4 | 0.9 | 2.1 | 1.1 | 1.3 | 2.1 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
30.10.17 | 7.1 | 11.2 | 1.7 | 1 | 1.1 | 1.2 | 0.8 | 1.1 | 1.7 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
28.11.17 | 7.1 | 11.2 | 2 | 1.3 | 1.1 | 1.7 | 0.8 | 1.9 | 2 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
19.12.17 | 7.1 | 11.2 | 1.6 | 1.5 | 1.2 | 1.9 | 1 | 1.6 | 1.9 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
31.01.18 | 7.1 | 11.2 | 1.3 | 1.2 | 0.9 | 1.3 | 1.1 | 1.5 | 1.5 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
24.02.17 | 7.1 | 11.2 | 1.7 | 1.1 | 1.3 | 1.3 | 0.8 | 1.3 | 1.7 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
21.03.18 | 7.1 | 11.2 | 1.5 | 1.4 | 1.2 | 1.1 | 1.5 | 1.4 | 1.5 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
28.04.18 | 7.1 | 11.2 | 1.7 | 1.5 | 1.5 | 2.3 | 1.7 | 1.9 | 2.3 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
03.05.18 | 7.1 | 11.2 | 1.7 | 1.5 | 1.5 | 2.3 | 1.6 | 1.9 | 2.3 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
26.05.18 | 7.1 | 11.2 | 3.6 | 2.5 | 4.2 | 6.1 | 6 | 11.2 | 11.2 | ALARM | *High vibrations are observed at motor DE bearing Bearing defects are indicated at motor bothe bearing. | *Inspect motor both bearings and replace on high priority.
28.05.18 | 7.1 | 11.2 | 1 | 1.1 | 1.3 | 2 | 1.4 | 1.4 | 2 | NORMAL | *After replacing the motor present Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.

## BFP-2
BFP-2 |  |  | SUMMARY
VELOCITY (mm/sec) |  |  | RMS
Date | NORMAL BELOW | ALARM ABOVE | MOTOR NDE-H | MOTOR NDE-V | MOTOR NDE-A | MOTOR DE-H | MOTOR DE-V | MOTOR DE-A | Max Vib. | STATUS | OBSERVATIONS & ANALYSIS | RECOMMENDATIONS
20.04.17 | 7.1 | 11.2 | 2.9 | 3.8 | 3.6 | 2.2 | 3.5 | 3 | 3.8 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
25.05.17 | 7.1 | 11.2 | 2.9 | 3.8 | 3.6 | 2.2 | 3 | 3.5 | 3.8 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
09.06.17 | 7.1 | 11.2 | 2.5 | 3.6 | 3.5 | 2.2 | 2.5 | 3.4 | 3.6 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
27.07.17 | 7.1 | 11.2 | 3.3 | 3.8 | 3.3 | 2.1 | 3.5 | 3.4 | 3.8 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
26.08.17 | 7.1 | 11.2 | 2.6 | 3.8 | 3.9 | 1.9 | 2.9 | 2.6 | 3.9 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
20.09.17 | 7.1 | 11.2 | 2.6 | 3.3 | 2.3 | 2.1 | 2 | 2.4 | 3.3 | NORMAL | *Spectrcum analysis indicating 1X & 2x line frequency at motor both bearings . * The Vibration levels are with in the limits. | * Monitor the vibration trend levels.
30.10.17 | 7.1 | 11.2 | 2.8 | 3.1 | 2.5 | 2.1 | 1.6 | 2.5 | 3.1 | NORMAL | *Spectrcum analysis indicating 1X &2x line frequency at motor both bearings . * The Vibration levels are with in the limits. | * Monitor the vibration trend levels.
28.11.17 | 7.1 | 11.2 | 2.1 | 3.5 | 3.3 | 1.8 | 3.3 | 3 | 3.5 | NORMAL | *Spectrcum analysis indicating 1X &2x line frequency at motor both bearings . * The Vibration levels are with in the limits. | * Monitor the vibration trend levels.
19.12.17 | 7.1 | 11.2 | 1.7 | 3.4 | 3.4 | 2.1 | 1.8 | 2.8 | 3.4 | NORMAL | *Spectrcum analysis indicating 1X &2x line frequency at motor both bearings . * The Vibration levels are with in the limits. | * Monitor the vibration trend levels.
31.01.18 | 7.1 | 11.2 | 2.2 | 2.6 | 2.6 | 1.8 | 1.9 | 2.4 | 2.6 | NORMAL | *Spectrcum analysis indicating 1X &2x line frequency at motor both bearings . * The Vibration levels are with in the limits. | * Monitor the vibration trend levels.
24.02.17 | 7.1 | 11.2 | 2.1 | 2.5 | 2.6 | 1.9 | 2 | 2.1 | 2.6 | NORMAL | *Spectrcum analysis indicating 1X &2x line frequency at motor both bearings . * The Vibration levels are with in the limits. | * Monitor the vibration trend levels.
21.03.18 | 7.1 | 11.2 | 2.2 | 2.6 | 2.8 | 2.1 | 1.6 | 1.8 | 2.8 | NORMAL | *Spectrcum analysis indicating 1X &2x line frequency at motor both bearings . * The Vibration levels are with in the limits. | * Monitor the vibration trend levels.
29.04.18 | 7.1 | 11.2 | 2.2 | 3.1 | 3.1 | 2.4 | 2.3 | 3.4 | 3.4 | NORMAL | *Motor replaced present vibration levels are with in limit. Spectrcum analysis indicating 1X & 2x line frequency at motor both bearings . *Minor bearing defects are indicated at motor both bearings. | * Monitor the vibration trend levels.
15.05.18 | 7.1 | 11.2 | 2 | 3.3 | 2.8 | 2.2 | 2.5 | 2.7 | 3.3 | NORMAL | *Vibration levels are with in limit. Spectrcum analysis indicating 1X & 2x at motor both bearings . *Minor bearing defects are indicated at motor both bearings. | * Monitor the vibration trend levels.
07.06.18 | 7.1 | 11.2 | 3.3 | 4.9 | 2.5 | 2.3 | 3.8 | 2.2 | 4.9 | ALARM | *Spectrum analysis is indicating bearing defects at motor NDE bearing. | *Inspect motor both bearings and replace on high priority.
08.06.18 | 7.1 | 11.2 | 2.5 | 1.5 | 2.4 | 2.2 | 1.8 | 2.2 | 2.5 | NORMAL | *Motor NDE bearing replaced present vibration levels are with in limit. Spectrcum analysis indicating 3X at motor both bearings . | * Inspect coupling gap and cross check the alignment. Monitor the vibration trend levels.

## KA#3 CHEST PUMP-2
NO:2 CHEST PUMP MOTOR |  |  | SUMMARY
VELOCITY (mm/sec) |  |  | RMS
Date | NORMAL BELOW | ALARM ABOVE | MOTOR NDE-H | MOTOR NDE-V | MOTOR NDE-A | MOTOR DE-H | MOTOR DE-V | MOTOR DE-A | Max Vib. | STATUS | OBSERVATIONS & ANALYSIS | RECOMMENDATIONS
07.04.17 | 4.5 | 7.1 | 1 | 0.8 | 1.2 | 0.8 | 0.6 | 1 | 1.2 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
09.05.17 | 4.5 | 7.1 | 1 | 1 | 1.5 | 0.9 | 0.6 | 1.1 | 1.5 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
17.06.17 | 4.5 | 7.1 | 1 | 0.8 | 1.2 | 1 | 0.6 | 1.1 | 1.2 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
15.07.17 | 4.5 | 7.1 | 1 | 1 | 1.2 | 1 | 1.9 | 1.2 | 1.2 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
14.08.17 | 4.5 | 7.1 | 1 | 0.7 | 1 | 1 | 0.6 | 1 | 1 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
11.09.17 | 4.5 | 7.1 | 1 | 1.2 | 1.1 | 0.7 | 0.9 | 1.1 | 1.2 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
25.10.17 | 4.5 | 7.1 | 1 | 0.8 | 1.4 | 0.7 | 0.7 | 1.1 | 1.4 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
08.11.17 | 4.5 | 7.1 | 1.5 | 1.9 | 2.1 | 1.5 | 2 | 1.6 | 2.1 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
08.12.17 | 4.5 | 7.1 | 1.3 | 1.2 | 1.6 | 1.1 | 1.1 | 1.5 | 1.6 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
08.01.18 | 4.5 | 7.1 | 1.4 | 1.1 | 2.2 | 1.3 | 1.2 | 1.7 | 2.2 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
12.02.18 | 4.5 | 7.1 | 1.2 | 1.2 | 1.8 | 1.2 | 1 | 1.5 | 1.8 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
13.03.18 | 4.5 | 7.1 | 1.3 | 1.3 | 1.8 | 1.1 | 1.4 | 1.6 | 1.8 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
07.04.18 | 4.5 | 7.1 | 1.4 | 1.3 | 1.2 | 1 | 1.6 | 1.4 | 1.6 | NORMAL | *Vibration levels are in satisfactory condition. | * Monitor the vibration trend levels.
09.05.18 | 4.5 | 7.1 | 8.8 | 3.9 | 7.3 | 8.7 | 6.8 | 5.9 | 8.8 | ALARM | *High vibrations are observed at motor both bearing. *Spectrum analysis is indicating 3X and 4X at motor both bearings. | * Inspect coupling and do the precision alignment. *After done alignment re-asses the health condition.
09.05.18 | 4.5 | 7.1 | 1.6 | 3.1 | 3.1 | 2.6 | 1.2 | 3 | 3.1 | NORMAL | *After replaced motor and done a precision alignment vibration levels are reduced. Vibration levels are in satisfactory condition. *Spectrum analysis is indicating 1X and 3X but severity is very low. | * Monitor the vibration trend levels.
11.05.18 | 4.5 | 7.1 | 2 | 2.5 | 2.6 | 1.9 | 1.2 | 2.4 | 2.6 | NORMAL | Vibration levels are in satisfactory condition. *Spectrum analysis is indicating 1X and 3X but severity is very low. | * Monitor the vibration trend levels.